[image: image4.png]



the hashemite kingdom of jordan
the jordanian electric power company limited

Specification JEP 20/2026


tender document for

36 kV O.H.L. ISOLATORS

	Tenderer's Name:
	____________________

	Address:

	____________________
____________________

	Closing Date:
	____________________

	Closing Time:
	____________________


mAY     2026

TABLE OF Contents

Page

4Form oF Tender


61.
scope of work


61.1
Definite work


72.
sITE AND DESIGN PARTICULARS


72.1
Particulars of system


72.2
Electrical designdata


72.2.1
System particulars


72.2.2
Equipment withstand voltage


82.2.3
Outdoor bushing and insulator creepage distances


82.2.4
Cable box clearances


92.2.5
Minimum clearance from live metal to oil pipework


92.2.6
Auxiliary power supplies


102.3
Site conditions


102.3.1
General


102.3.2
Elevation


102.3.3
Earthquakes


102.3.4
Snow


102.3.5
Hail


112.3.6
Air temperature (Degrees Centigrade)


112.3.7
Rainfall amount (millimeter)


112.3.8
Relative humidity (%)


122.3.9
Mean wind speed (m/s)


122.3.10
Clouds “oktas”


122.3.11
Fog “visibility 1 km or less”


122.3.12
Dust “visibility 1 km or less”


122.3.13
Thunderstorms


133.
GENERAL TECHNICAL CLAUSES


133.1
Standards


133.2
Design and standardization


143.3
Galvanizing


153.4
Copper conductors


153.5
Aluminium and aluminium alloys


153.6
Labels and identification plates


173.7
Bolts and nuts


183.8
Cleaning and painting


183.8.1
External surfaces at works


183.8.2
Internal surfaces


193.9
Insulating oil and gas


193.10
Prevention of acidity


193.11
Fire precautions


193.12
Corona and radio interference


193.13
Locking devices and padlocks


193.14
Tools


203.15
Erection marks


203.16
Operating and maintenance instructions


203.17
Spare parts


203.18
Manufacturing experience and qualifications


203.19
Quality Assurance system


214.
33&11 kV OVERHEAD LINE EQUIPMENT


214.1
Type of Switchgear


214.2
Current Ratings


214.3
Clearances


214.4
Isolators


224.5
Switch-Isolators


235.
INSPECTION AND TESTS


235.1
General


235.2
Isolators and Earth Switches


235.2.1
Routine Tests


235.2.2
Type Tests


Error! Bookmark not defined.SCHEDULE a


25SCHEDULE B


26SCHEDULE C


SCHEDULE D
28
29SCHEDULE e


30SCHEDULE e


32schedule g1


34schedule g2


Error! Bookmark not defined.SCHEDULE h


35schedule j


36schedule K


37schedule l


38schedule n



LIST OF ABBREVIATIONS

	BS
	British Standards

	IEC
	International Electrotechnical Commission

	JEPCO
	The Jordanian Electric Power Company Limited


Form oF Tender
THE JORDANIAN ELECTRIC power COMPANY LIMITED
TENDER FOR CONTRACT NO JEP 20/2026
36 kV O.H.L. ISOLATORS
(Tenderers are required to fill up the blank spaces in this Tender Form and Appendix)

The General Manager

The Jordanian Electric Power Company Limited

PO Box 618

Amman 11118

The Hashemite Kingdom of Jordan

1.
Having examined the Drawings, Conditions of Contract, Specification and Schedules for the execution of the above-named Goods, we, the undersigned, offer to execute, complete and remedy defects in the whole of the said Goods in conformity with the said Drawings, Conditions of Contact, Specification and Schedules for the sum of 
…………

(Figures…………..………………….)
or such other sum as may be determined in accordance with the said conditions.

2.
We agree to abide by this Tender for the period of 120 days from the date fixed for receiving the same and it shall remain binding upon us and may be accepted at any time before the expiration of that period.  

3.
We undertake if our Tender is accepted to complete and deliver the whole of the Goods comprised in the Contract within 
…………… week(s) subject to the said Conditions.

4.
If our Tender is accepted we will obtain the guarantee of an Insurance Company or Bank or other sureties (to be approved by you) to be jointly and severally bound with us in a sum not exceeding 10 per cent of the above named sum for the due performance of the Contract under the terms of a Bond to be approved by you.  

We propose the following Bank or Insurance Company as surety (or sureties) in this respect:

(
)

(
)

(
)

5.
Unless and until a formal Agreement is prepared and executed, this Tender, together with your written acceptance thereof, shall constitute a binding Contract between us.

6.
We undertake to provide a defects guarantee period as stated in Clause 15 of the conditions of contract for each section of the Plant from the date of delivery to the Port of Aqaba, or such other destination that may be stated in the Contract.  

7.
We understand that you are not bound to accept the lowest or any Tender you may receive.

8.
Tenderers must give details of their representative or associated companies in the Hashemite Kingdom of Jordan who will deal with this Contract if it is awarded to the Tenderer:

Name and Full Address of Representative:



Telephone Number



Fax Number



Telex Number



9.
APPENDIX TO TENDER

	
	Clause
	

	Time for completion
	10.1
	
 weeks

	Amount of Bond or Guarantee
	 7.1
	10% of Contract sum 


	
	11.1
	Full replacement value +
 10%

	Amount of reduction per week of delay
	23.1
	1% 

 of Contract Price

	Maximum reduction
	23.1
	10% 

of Contract Price

	Defects Liability Period
	15.2
	


	Use of Goods assumed
	
	

24 hours per day

	Name and address of Tenderer’s Bank
	
	



Dated this 

day of 


200   

Signature 

in the capacity of 


duly authorized to sign tenders for and on behalf of 


Witness

Address


Occupation


1.
scope of work

1.1
Definite works
The works shall comprise the design, manufacture, testing and delivery to the Port of Aqaba,  The Hashemite Kingdom of Jordan of the equipment listed in this Specification, equipment in accordance with the Conditions of Contract at prices stated in the Schedule of this Specification, together with the provision of certain specified spares.  

	Item No.
	Description
	Qty.

	1.
	36 kV, 400 A, 25 kA for 3 seconds, 3-phase pole mounted load break isolator switches.
	250
 Set

	1.1
	Ditto as in item1 but with 630A current rating.
	


Notes: 
· Minor deviations shall be subject to the approval by JEPCO's Engineer.

· JEPCO has the right to choose either item1 or item 1.1 or a combination of them.

· Documents to be submitted as an integral part of the offer, and to be evaluated with the tender:

1. Full technical details, drawings and catalogues.

2. Type test certificates from any European STL member laboratory (KEMA, CESI, and IPH) or equivalent.

3. Tracking and erosion – 1000 h salt fog test according to the latest edition of IEC 62217.
4. Fully detailed reference list with contact details.

5. ISO certificate. And any documents that will assist in the evaluation.
· Full Compliance sheet/ deviations shall be submitted with the offer.

2.
sITE AND DESIGN PARTICULARS

2.1
Particulars of system

The following are the particulars of the systems on which the equipment covered by the Specification shall operate:-
i.
33 kV 3-phase at a frequency of 50 Hz with the neutral point resistance earthed.  

ii.
11 kV 3-phase at a frequency of 50 Hz with the neutral point solidly earthed.  

iii.
415 volts 3-phase and neutral at a frequency of 50 Hz with the neutral point solidly earthed.  

2.2
Electrical design data

2.2.1
System particulars

	Nominal system voltage between phases
	
kV
	
33
	
11
	
0.415

	Highest system voltage
	kV
	36
	12
	0.440

	System fault level
	kA
	31.5
	25
	50*

	Earthing system
	

	Resistance earthed
	Solidly
earthed
	Solidly
earthed

	System frequency
	Hz
	50
	50
	50


2.2.2
Equipment withstand voltage

	i.

	Outdoor bushings, insulators and pole mounted transformers

	
	Impulse withstand voltage (1.2/50µs wave) peak
	
kV
	
250
	
95
	
-

	
	Power frequency withstand voltage
	
kV
	
95
	
38
	
-

	ii.

	All other equipment excluding pole mounted transformers

	
	Impulse withstand voltage (1.2/50µs wave) peak
	
kV
	
170
	
75
	
-

	
	Power frequency withstand voltage
	
kV
	
75
	
28
	
-


2.2.3
Outdoor bushing and insulator creepage distances

	Minimum creepage distance
	mm
	1089
	400
	-

	Protected creepage distance
	mm
	545
	160
	


2.2.4
Cable box clearances

The minimum cable box clearances under compound or oil shall be as follows:-

	Nominal system voltage
	kV
	33
	11
	Below 1

	Minimum clearance between phases
	
mm
	
125
	
45
	
20

	Minimum clearance phase to earth
	
mm
	
100
	
32
	
20

	Minimum creepage distance phase to earth over cable surface
	

mm
	

250
	

125
	

26

	The minimum cable box clearances in air-filed, air-insulated boxes, live metal to live metal and unshrouded shall be as follows:-

	Nominal system voltage
	kV
	33
	11
	

	Minimum clearance between phases
	
mm
	
356
	
178
	

	Minimum clearance phase to earth
	
mm
	
222
	
115
	

	Minimum creepage distance phase to earth over cable tail surface
	

mm
	

800
	

450
	

	The minimum cable box clearance in air-filled boxes with shrouded insulation termination is as follows:-

When this type of termination is used the dimensions will be based on the termination manufacturers recommendations and be subject to approval by the Engineer.  


2.2.5
Minimum clearance from live metal to oil pipework (including conservator and pressure relief devices on transformers)

	Highest system voltage
	kV
	36
	12

	Minimum clearance
	mm
	485
	250

	Apart from the clearances detailed under this item, no phase or earth clearances are specified for transformers where an impulse voltage test level is specified.  


2.2.6
Auxiliary power supplies

	Supply voltage for auxiliary equipment
	i.
400 volt, 3 phase and Neutral 50 Hz

	
	ii.
110 volts DC 2 wire


2.3
Site conditions
2.3.1
General

The site conditions shall be assumed to be as follows for the purposes of Tender preparation.  

2.3.2
Elevation

766 meters above sea level - Amman Airport at which all the climatic observations used were taken by the Jordanian Ministry of Transport Meteorological Department.  

2.3.3
Earthquakes

Amman is classified as Seismic Zone 2.  

2.3.4
Snow

Snowfall in cm at Locations in the Amman Area in 10 years 1972-1982.  

	Area
	No of days of snowfall/year
	Greatest depth of snow (cm)

	Wadi Dhuleil
	1-04
	10

	Amman Airport
	1-13
	30

	Jordan University
	1-13
	60

	Naur
	1-13
	45

	Ma
	1-04
	25


2.3.5
Hail

Not a normal occurrence but occurs on average 3.2 days per year.  

	Station: Amman Airport
	31 deg 59 min NORTH
35 deg 59 min EAST
766 m above sea 

	Period: 1923 - 1985
	


2.3.6
Air temperature (Degrees Centigrade)

	
	JAN
	FEB
	MAR
	APR
	MAY
	JUN
	JUL
	AUG
	SEP
	OCT
	NOV
	DEC
	YEAR-LY

	Mean monthly
	
7.9
	
9.
	
11.7
	
15.9
	
20.5
	
23.6
	
25.1
	
25.4
	
23.5
	
20.4
	
14.9
	
9.8
	
17.3

	Mean daily max
	
12.4
	
13.8
	
17.4
	
22.5
	
27.8
	
30.9
	
31.9
	
32.4
	
30.7
	
27.2
	
20.6
	
14.5
	
23.5

	Mean daily min
	
3.5
	
4.2
	
6.1
	
9.3
	
13.3
	
16.3
	
18.2
	
18.3
	
16.2
	
13.6
	
9.3
	
5.1
	
11.1

	Absolute max
	26.3
	29.4
	32.5
	39.2
	40.6
	42.8
	42.4
	42.8
	40.6
	37.4
	.8
	27.3
	42.8

	Absolute min
	-7.5
	-6.5
	-3.9
	0.0
	3.0
	7.8
	11.0
	11.5
	8.9
	4.9
	-3.2
	-5.3
	-7.5

	Design ambient temperature is 45 degrees centigrade


2.3.7
Rainfall amount (millimeter)

	Mean monthly
	
64.5
	
63.9
	
44.7
	
16.1
	
3.7
	
0.03
	
TR
	
TR
	
0.4
	
5.8
	
28.6
	
48.6
	
276.3

	Max amount in a month
	

235.2
	

190.8
	

168.7
	

151.3
	

30.6
	

1.1
	

TR
	

TR
	

15.4
	

54.6
	

136.8
	

179.8
	

476.5

	Max amount in one day
	

75.6
	

80.0
	

66.2
	

52.4
	

24.1
	

1.1
	

TR
	

TR
	

15.4
	

40.5
	

79.4
	

73.6
	

80.0


2.3.8
Relative humidity (%)

	Mean monthly
	
70.0
	
67.0
	
60.0
	
50.0
	
39.0
	
37.0
	
40.0
	
43.0
	
47.0
	
46.0
	
56.0
	
68.0
	
52.0

	Max relative humidity reaches 100 per cent especially during rainy intervals and night, while min relative humidity drops to less than 10 per cent on some occasions especially during Khamsinic conditions (22 March - 10 May).  


2.3.9
Mean wind speed (m/s)

	Direction (deg)
	
227
	
241
	
251
	
254
	
275
	
276
	
278
	
282
	
284
	
267
	
226
	
222
	
264

	Mean monthly
	
3.2
	
3.3
	
3.4
	
3.6
	
3.3
	
3.6
	
3.9
	
3.4
	
2.6
	
2.2
	
2.4
	
2.9
	
3.2

	Max wind gust
	

35
	

28
	

30
	

31
	

24
	

22
	

19
	

17
	

17
	

26
	

26
	

34
	

…..


2.3.10
Clouds “oktas”

	Mean amount
	
3.8
	
3.5
	
3.4
	
3.2
	
1.9
	
0.6
	
0.3
	
0.3
	
0.7
	
1.5
	
2.6
	
3.4
	
2.1

	No cloudy days
	

4.7
	

3.1
	

3.8
	

2.5
	

0.7
	

0.0
	

0.0
	

0.0
	

0.0
	

0.3
	

1.0
	

3.6
	

19.5


2.3.11
Fog “visibility 1 km or less”

	Mean no of days
	
1.5
	
0.7
	
0.4
	
0.2
	
0.0
	
0.0
	
0.0
	
0.0
	
0.0
	
0.1
	
0.3
	
0.7
	
3.9

	Max number of days with fog 11 days per year


2.3.12
Dust “visibility 1 km or less”

	Mean no of days
	
0.4
	
0.1
	
0.6
	
0.2
	
0.2
	
0.0
	
0.0
	
0.0
	
0.0
	
0.0
	
0.2
	
0.1
	
1.7

	Max number of days with dust 6 days per year


2.3.13
Thunderstorms

	Mean no of days
	
0.4
	
0.4
	
1.3
	
0.8
	
0.6
	
0.0
	
0.0
	
0.0
	
0.4
	
1.2
	
1.1
	
0.4
	
6.6

	Max number of days with thunder storms 17 days per year


3.
GENERAL TECHNICAL CLAUSES

3.1
Standards

Although  American, British or IEC standards for workmanship, material and equipment have been selected in these Specifications as a basis of reference, standards and specifications of other countries and recommendations of  other standard international organisations will be acceptable provided they are substantially equivalent to, or higher  than, the designated standards and provided furthermore that the Supplier submits for approval details of the specifications heproposes to use.

When IEC recommendations or national standards are referred to the Edition shall be that current at the date of Tender, together with any amendments issued to that date.  

If requested by the Engineer, the Contractor shall supply at his own expense three copies in English and one in the original language of any national standards which are applicable to the Contract.  

3.2
Design and standardization

The Goodshall be designed to facilitate inspection, cleaning and repairs, and for operation in which continuity of service is the first consideration. All apparatus shall be designed to ensure satisfactory operation under the atmospheric conditions prevailing at the Sites and under such sudden variations of load and voltage as may be met with under working conditions on the system , and short circuits, including those due to faulty synchronising within the rating of the apparatus.

The design shall incorporate every reasonable precaution and provision for the safety of all those concerned in the operation and maintenance of the Goods and of associated works supplied under other Contracts.

All material used shall be of the best quality and of the class  most suitable for working under the conditions specified and shall withstand the variations of  temperature and atmospheric conditions arising under working conditions without distortion or deterioration or the setting up undue stresses in any part, and also without affecting the strength and suitability of the various parts for the work which they have to perform. No welding, filling or plugging of defective parts will be permitted without the sanction in writing of the Engineer.

Corresponding parts liable to renewal shall be interchangeable. When required by the Engineer, the Supplier shall demonstrate this quality.

All apparatus shall operate without undue vibration and with the least practicable amount of noise. 

Cast iron shall not be used for chambers of oil-filled apparatus or for any part of the equipment which is in tension or subject to impact stresses except where it can be shown that service experience has been satisfactory with the grade of cast iron and the duty proposed.

Operating boxes, kiosks, cubicles and similar enclosed compartmentsforming part of auxiliary equipment shall be adequately ventilated to restrict condensation, and,where required  by  the  Engineer, suitable low-temperature heaters shall be provided. All contactor or relay coils and other parts shall be suitably protected against corrosion.

All outdoor apparatus, including bushing insulators and fittings shall be so designed as to avoid pockets in which water can collect.

The underside of all tanks shall be ventilated in an approved manner to prevent corrosion.

Accessible  means shall be provided for the easy lubrication of all  bearings  and  where necessary, of any mechanism or moving part. Grease lubricators shall be fitted with hexagon nipples.

All mechanisms shall, when  necessary, be constructed of stainless steel, brass or gunmetal to prevent sticking due to rust or corrosion.

All taper pins used in any mechanism shall be of the split type.

The busbars, connections, isolators, fuses, contacts, cable boxes,  trunking connections etc,. which form part of the Contract Works shall not exceed the temperature rise values specified in the relevant IEC publication or equivalent national standard. 

All connections and contacts shall be of ample section and surface for carrying continuously the specified currents without undue heating, and shall be secured by bolts or set screws of ample size,  fitted  with locking devices of approved type and material.

All rubbing or wearing surfaces shall be machine surfaced. Joints employing a gasket material shall be so consturcted that the packing is  maintained under sufficient compression in all parts,  so that an efficient joint can be made  without the use of jointing compounds.  Gasket material shall be of the minimum thickness necessary and of approved composition.

All apparatus shall be designed to obviate  the  risk  ofaccidental  short circuit  due to animals,  birds, and vermin. Openings in ventilated enclosures shall be so constructed to prevent the entry of vermin and insects.

3.3
Galvanizing

Galvanizing shall be applied by the hot dipped process.  The preparation for galvanizing and the galvanizing process shall not adversely affect the mechanical properties of the material being coated.  The zinc coating shall be clean, of uniform thickness and free from defects.  

When zinc spray coating is used, surfaces shall be shot blasted before spraying.  

Drilling, punching, cutting, bending and removal of burrs shall be completed before galvanizing/zinc spray coating.  

The average thickness of the zinc coating shall be equivalent to not less than 0.6 kg/m2 of zinc for all surfaces, except steel wires.  

The thickness of the zinc coating for steel wires shall be in accordance with a national standard and shall be approved by the Engineer.  

Material on which galvanizing has been damaged shall be re-dipped unless, in the opinion of the Engineer, the damage is local and can be repaired by applying a coat of galvanizing repair paint.  Where such a repair is authorized, tdamaged area shall be cleaned bwiping with clean rags saturated with mineral spirits or xylene followed by wire brushing.  After wire brushing, the area shall be re-cleaned with solvent to remove residue and shall be given a minimum of two coats of zinc rich paint in accordance with the manufacturer’s instructions.  

Samples selected by the Engineer of all galvanized material shall be subjected to the galvanizing tests set out in the appropriate material standard (eg BS 443/BS 729).  

Sheradizing or other similar processes shall not be used unless expressly approved by the Engineer.  

Surfaces in contact with oil shall not be galvanized or cadmium plated.  

3.4
Copper conductors

All copper conductors shall be composed of high conductivity electrolytic copper having a conductivity of not less than 99.9 per cent of the International Agreed Copper Standard (IACS).  

3.5
Aluminium and aluminium alloys

Aluminium shall be of high commercial quality. The composition, including the percentage and nature of any impurities, shall be stated in the schedules.  

All aluminium alloys shall be of approved compositions as stated in the schedules.  

Aluminium and aluminium alloy castings shall be sound and free from porosity.  

3.6
Labels and identification plates

All equipment shall be clearly and permanently labelled, to the approval of the Engineer, in English, unless otherwise specified.  Where labels are provided in diagrammatic form, any inscription shall be in English unless otherwise specified.  

A label shall be permanently fixed to each item of equipment in a clearly visible position stating:  

Property of The Jordanian Electric Power Co Ltd
Year of Manufacture

All control and relay panels, marshalling boxes, kiosks, distribution boxes and other cubicles shall be labelled to show the circuit with which it is associated.  These labels shall be fitted to the front and back of all equipment.  

Labels, number plates and their fixing screws, for outdoor use, shall be of stainless steel or other corresistant material.  Where the use of vitreous enamelled labels is approved, the whole surface including the back and edges shall be properly covered and protewasshall be provided front and back on the fixing screws.  

The materials of the labels and number plates, for indoor and outdoor use, shall be approved by the Engineer and shall be fixed so as to prevent buckling due to temperature and humidity variations.  

Danger notices shall have red lettering on a white background and shall be in English and Arabic.  

Unless otherwise approved by the Engineer, all other labels and number plates shall have black inscriptions on a white base colour.  

Labels for similar equipment shall be of uniform appearance and the dimensions and size of letter shall be to the approval of the Engineer.  
Each equipment shall be marked with its function, manufacturer's name or trade mark and the code type number together with the batch or serial number.

Each detachable unit  shall be either marked so as to enable it to be identified with the parent equipment, or else marked with the manufacturer's name and type number or code number and where definable, its function.

Each Unit and sub-unit mounting position shall be marked to indicate  the type of unit or sub-unit to be located in that position. Addmarkings may be required for apparently identical units or sub-units having different pre-set characteristics.

Component reference numbers shall be marked adjacent to the component. Where this is impossible, components shall be identifiable from the drawings provided by the Contractor.

The following shall be marked in all instances:-

(a)
Fuse. The rating and circuit identification of each fuse shall be marked adjacent to the fuse base.

(b)
Control and Indicating Devices. The function  of each control and indication device shall be marked. The caption and its arrangement shall be subject to the approval of the Engineer.

(c)
Pre-set Controls. The circuits reference and if possible, the function, shall be marked adjacent to each pre-set control in a position where it will be clearly visible while the adjustment is being made.

(d)
Connectors. The diagram reference number shall be marked on, or adjacent to each connector.

(e)
Test Points shall be individually marked with the diagram reference number.

All junction boxes shall include a record pasted inside the lid showing the terminal allocation.

Each terminal of a screw type terminal block shall bear the identification marking either on the body of the block, or adjacent to it. All other terminal blocks shall be marked with their circuit designations and rows shall be marked to identify each connection to the approval of the Engineer.

All wiring shall be identifiable by an approved colour code, ferrules marked with the nomenclature adopted for these conductors, on the manufacturer's diagrams, or by circuit reference at the terminals.

3.7
Bolts and nuts

All bolts, studs, screw threads, pipe thread, bolt heads and nuts shall be of ISO metric standard type.  
Except for small wiring, current carrying terminal bolts or studs, for mechanical , shall not be less than 6 mm in diameter.

All nuts and pins shall be adequately locked.

Wherever possible bolts shall be fitted in such a manner that in the event of failure of locking resulting in the nuts working loose and falling off, the bolt will remain in position.

All bolts, nuts and washers placed in outdoor positions shall be treated to prevent corrosion of the threads and electrolytic action between dissimilar metals.

Where bolts are used on external horizontal surfaces where water can collect, methods of preventing the ingress of moisture to the threads shall be provided.

Each bolt or stud shall project at least one thread but not more than four threads through its nut, except when otherwise approved for terminal board studs or relay stems.  If bolts and nuts are placed so that they are inaccessible by means of ordinary spanners, special spanners shall be provided.

The length of the screwed portion of the bolts shall be such that no screw thread may form part of a shear plane between members.

Taper washers shall be provided where necessary.

3.8
Cleaning and painting

Before painting or filling with oil, gas or compound, all ungalvanized parts shall be thoroughly cleaned, free from rust, scale, burrs, grease and moisture and all external rough surfaces on casting shall be filled.  

The following minimum painting requirements shall apply to all ferrous parts unless the supplier can show, to the satisfaction of the Engineer, that any alternative he proposes is in all respects equal or superior to the specified requirements:  

3.8.1
External surfaces at works

	All ungalvanized surfaces, other than nuts, bolts and washers, which may be removed for maintenance purposes, for use outdoors
	i.
One priming coat of corrosion inhibiting paint applied immediately after cleaning  

ii.
Two coats of non-glossy, oil- and weather-resisting paint applied after inspection and testing and before despatch

iii.
One finishing coat of glossy oil and water resisting non-fading paint before despatch. 

	Exposed, ungalvanized nuts, bolts and washers which may be removed for maintenance purposes, for use outdoors
	One coat of oil - and weather-resisting, non-fading paint applied.  

	Panels, cubicles, kiosks and apparatus boxes, for use indoors
	Three coats of paint, the colour and finish of the final coat to be to the approval of the Engineer.  

Grey colour is preferable.  


3.8.2
Internal surfaces

	Apparatus
	Painting

	Oil filled chambers and tanks
	One coat of oil resisting varnish or paint

	Kiosks and apparatus boxes for use outdoors
	Three coats of paint, the final coat being an anti-condensation finish coloured white or light grey  

	Cubicles, kiosks and apparatus boxes for use indoors
	Three coats of paint, the final coat being a white or light colour.  


Successive coats of paint shall be easily distinguishable by shade of colour and shall be applied to a clean, dry and properly prepared surface.  Each coat shall be compatible with thprevious coat.  

All paintwork which has bedamaged during transport or erection shall be made good to the approval of the Engineer.  

The colour and shade of all painted external surfaces shall be to the approval of the Engineer.  

3.9
Insulating oil and gas

Unless otherwise specified, sufficient oil or gas shall be supplied to fill all equipment provided under this Contract.  The oil or gas shall be of appropriate type and suitable in all respects for use in the equipment when it is operated under the conditions laid down in this Specification.  The insulating medium used shall comply with the relevant IEC Specification.  

3.10
Prevention of acidity

The design, and all materials and process used in construction of the equipment, shall be such as to reduce to a minimum the risk of development of acidity in the oil or gas.  

3.11
Fire precautions

All apparatus, connections and cabling shall be designed and arranged to minimize the risk of fire and any damage which might be caused in the event of fire.  

3.12
Corona and radio interference

All equipment shall be designed so as to minimize corona or other electrical discharge and radio interference.  

3.13
Locking devices and padlocks

All padlocks, locks and keys required to secure switchgear and other equipment shall be supplied on this Contract.  

Access doors to equipment including circuit breakers, isolating devices, screened enclosures, cubicles and marshalling kiosks and all equipment operating handles, local control and selector switches, valves, switchgear shutters and maintenance positions shall be lockable.  

All padlocks and other locks shall be provided with two identical keys and both the key and the lock shall be impressed with the manufacturer’s serial number.  Except where a master key is specially requested or it has been otherwise agreed, it shall be impossible to open any padlock or lock with the key of any other padlock or lock provided on this Contract.  

When requested, wall mounting lockable cabinets with glazed doors, suitable for accommodation of padlocks and keys whilst not in use, shall be provided.  They shall be mounted in approved positions and shall be labelled in a similar manner to the keys.  The engraving on all labels shall be in accordance with a scheme to be agreed with the Engineer.  

3.14
Tools

The Supplier shall provide any special tools that may be required for making adjustments to equipment during normal operation and maintenance.  These tools are to be of alloy steel and shall be contained in steel boxes, complete with locks and keys.  

All tools shall be stamped in an approved manner for identification purposes.  

3.15
Erection marks

All plant that requires assembly at Site shall have distinguishing marks on it to facilitate erection and to identify the material in relation to drawings, material lists or shipping documents.  All marks shall be legible and easily visible.  Where relevant, erection marks shall be stamped before galvanizing and shall be clearly visible after galvanizing.  

3.16
Operating and maintenance instructions

Operating and maintenance instructions form part of this Contract and shall be provided in accordance with the Conditions of Contract.  

3.17
Spare parts

Particulars of spare parts, which may or may not form part of the Contract at the Engineer’discretion, shall be given in Schedule J.  

3.18
Manufacturing experience and qualifications

The Tenderer shall provide documentary evidence confirming that equipment of identical design and rating to that offered against this document has been in production for a minimum of 10 years. In addition a list is to be provided with full address (Telephone & Fax) numbers and e-mails of users with service experience of equipment identical to that offered.

3.19
Quality Assurance system

The supplier must hold ISO 9002 (alternatively ISO 9001) certification of their quality assurance procedures.  Evidence of such certification must be submitted with the Tender.  

Where an equivalent certification to ISO 9002 (alternative ISO 9001) is offered, details of the system, the certification body and the frequencyand type of audits, both internal and external, shall be submitted with the Tender.  The equivalent certification shall be subject to review, evaluation and approval by JEPCO or its appointed representative(s).  

4.
36 kV OVERHEAD LINE EQUIPMENT

4.1
Type of Switchgear

The switchgear shall be of the open type suitable for continuous operation outdoors under the climatic conditions existing at the sites.

4.2
Current Ratings

Unless otherwise approved the complete equipment shall be capable of carrying a through fault current equivalent to the specified rated breaking capacity of the load break isolators or circuit breakers for 3 seconds and shall also be capable of carrying continuously the rated normal currents specified without damage or overheating of any part.

4.3
Clearances

The clearances and positions of apparatus including the access facilities shall permit safe maintenance of any section of the apparatus while the remaining sections are alive.

The height from the ground of any live part of the equipment shall be not less than 2.45 meters plus the length of the supporting insulator or the bushing insulator.

4.4
Isolators

Isolators shall be arranged to permit safe maintenance of any section of the equipment when the remainder are alive. They shall be suitable for operation while the equipment is alive and designed for them to make or break the charging currents of open busbars and connections or load currents shared by parallel circuits.

The minimum total length of air gap between terminals of the same pole with the isolator open shall be designed to provide an impulse withstand level in excess of that specified for the insulation of the substation to earth. Such withstand shall preferably be not less than 15% greater than the withstand to earth and shall in no case be less than the minimum corresponding figure for the isolating distance as given in IEC 62271-102.

Where manual operating mechanisms are required operation shall be possible from ground level.

Isolator mechanisms shall be so designed that the primary contacts can not be opened by forces due to currents passing through them, and shall be self-locking in both the "open" and "close" positions. The mechanism shall open and close all poles simultaneously.

Service conditions require that isolators shall remain alive and in service without being operated and without maintenance for periods of up to two years in corrosive atmosphere over a wide temperature range. In such conditions the contacts will be expected to remain capable of carrying this rated normal and short-circuit currents without overheating or welding. After such periods the maximum operating torque required shall not exceed twice the torque required during type tests and should be within the capabilities of one man (i.e. approx. 340 Nm).

When made of steel or malleable iron, operating boxes, handles, rods, tubes and other fittings for outdoor type equipment shall be galvanised. Main bearings, pins etc. shall preferably be of the self lubricating type to reduce routine maintenance to a minimum.

4.5
Switch-Isolators

Switch-isolators shall be capable of making and carrying short-circuit currents and making and breaking inductive and capacitive current for the purposes of transformer, reactor, capacitor, line or cable switching duties as detailed in this Specification.

Switch-isolators shall satisfy the requirements relevant to isolators with reference to safe maintenance clearances and insulation level across their opened contacts.

Switch-isolators shall be restrike-free in respect of the current breaking requirements when capacitive switching duties are required. All switch-isolators shall control and minimize pre-arcing in respect of current making duty. Switching over-voltages shall not exceed the maximum which is stated in the Specification as being the highest permissible over-voltage.
5.
INSPECTION AND TESTS

5.1
General

All equipment is subject to inspection by the Engineer at the Manufacturer's Works. Not less than fourteen days notice of all tests shall be given to the Engineer in order that he may present if he so desires. The Supplier shall make the tests specified and any others required by the Engineer to show that the Goods comply with the Specification and with the appropriate Schedules.  The tests shall be made at the Supplier's expense.

No passing of the plant or materials by the Engineer shall relieve the Supplier of his responsibility.  The Supplier shall also be responsible for proper carrying out of all tests of work and of plant and material carried out or supplied by a Sub-contractor to the  same extent as if the work, plant or material were carried out or supplied by the Supplier himself.

If, due to the Goods and/or component materials not complying with this Specification further tests are necessary, the Supplier shall pay all additional costs which may be incurred in re-testing. 

During the execution of the Contract, test specimens, if required by the Engineers, shall be taken from the materials for the purpose of check tests or analyses for testing and forwarded at the expense of the supplier to the Testing Authorities selected by the Engineer. 

Six copies of the Supplier's records of all tests shall be given to the Engineer. 

All material which is specified for tests at the Manufacturer's Works shall satisfactorily pass such test before being painted.

All instruments used for the purpose of testing shall be approved and, if requierd, shall be calibrated at the expense of the Supplier by such body as may be approved. 

Where type tests are specified below they shall be carried out in the presence of the Engineer. Alternatively the Supplier shall provide certificates showing that such tests have been carried out satisfactorily on apparatus similar to that being supplied.

5.2
Isolators and Earth Switches

5.2.1
Routine Tests

In accordance with the requirements of IEC 62271-102 and IEC 62271-103 where applicable.

5.2.2
Type Tests

In accordance with the requirements of IEC 62271-102 and IEC 62271-103 where applicable.
If required by the Engineer, a completely assembled unit of each type shall be mounted on its steel structure and operational tests carried out.
SCHEDULE a
ITEMS OF THE CONTRACT FOR THE PURPOSES OF
PAYMENT AND TAKING OVER

For purposes of evaluation of the tender, the time from commencement date within which the material is required to be delivered to the port of Aqaba shall be 16 weeks.
	Item No.
	Description
	Qty.

	1.
	36 kV, 400 A, 25 kA for 3 seconds, 3-phase pole mounted load break isolator switches.
	250
 Set

	1.1
	Ditto as in item1 but with 630A current rating.
	


Notes: 
· Minor deviations shall be subject to the approval by JEPCO's Engineer.

· JEPCO has the right to choose either item1 or item 1.1 or a combination of them.

· Documents to be submitted as an integral part of the offer, and to be evaluated with the tender:

1. Full technical details, drawings and catalogues.

2. Type test certificates from any European STL member laboratory (KEMA, CESI, and IPH) or equivalent.

3. Tracking and erosion – 1000h salt fog test according to the latest edition of IEC 62217.
4. Fully detailed reference list with contact details.

5. ISO certificate. And any documents that will assist in the evaluation.
· Full Compliance sheet/ deviations shall be submitted with the offer.

SCHEDULE B
TIME PERIODS FOR PROCUREMENT, DESIGN, MANUFACTURE,
INSPECTION, TESTING, COMAND DELIVERY

(To be completed by the Tenderer)

Note 1

All time periods are weeks from date of Contract Placement.

Note 2

For purposes of Tender Evaluation,  the time from coomencement date within which the material is required to be delivered to the Port of Aqaba shall be 16 weeks.

	
Description
	Item 1
weeks
	Item 1.1
weeks

	Time within which all arrangement and equipment drawings shall be submitted for approval.

Time within which all material shall be available for final inspection and testing in works.

Time within which the plant shall be packed and delivered to the Docks (FOB).

Time within which the plant shall be delivered CFR Aqaba.
	
……………..


……………..


……………..

……………..
	
……………..


……………..


……………..

……………..


SCHEDULE C
MANUFACTURERS AND PLACES OF MANUFACTURE,
TESTING AND INSPECTION

(To be completed by the Tenderer)

	
Item 
No.
	

Description
	

Manufacturer
	
Place of
Manufacture
	Place of Testing & Inspection*

	1.
	36 kV pole mounted type isolating switches

· Mechanism

· Steel work.

· Silicon Rubber Insulator.

· Interrupter head
	……………

……………

……………
……………
	……………

……………

……………
……………
	……………

……………

……………
……………

	1.1
	36 kV pole mounted type isolating switches

· Mechanism

· Steel work.

· Silicon Rubber Insulator.

Interrupter head
	……………

……………

……………
……………
	……………

……………

……………
……………
	……………

……………

……………
……………


SCHEDULE D
technical data
Overhead Line equipment

(To be completed by the Tenderer)
	Pole Mounted Load Break Isolators
	Item1
	Item1.1

	1.
	Equipment
	
	…………..
	…………..

	2.
	Manufacturer
Origin
	
	…………..
	…………..

	
	
	
	…………..
	…………..

	3.
	Type
	
	…………..
	…………..

	4.
	Manufacturer's Reference.
	
	…………..
	…………..

	5.
	Type of operating Mechanism.
	
	…………..
	…………..

	6.
	Rated Voltage:
	
	
	

	
	a) Nominal System Voltage
	V
	…………..
	…………..

	
	b) Highest System Voltage
	V
	…………..
	…………..

	7.
	Rated Normal Current
	A
	…………..
	…………..

	8.
	Maximum Breaking Load
	A
	…………..
	…………..

	9.
	a) Rated short time current 
	KA
	…………..
	…………..

	
	b) Rated maximum duration of short circuit
	sec
	…………..
	…………..

	
	c) Rated short circuit making capacity
	KA
	…………..
	…………..

	10.
	Breaking capabilities of:
	
	
	

	
	a) Transformer off load
	A 
	…………..
	…………..

	
	b) Transformer full load 
	A
	…………..
	…………..

	
	c) Line charging
	A
	…………..
	…………..

	11.
	Maximum resistance between main circuit
	m ohm
	…………..
	…………..

	12.
	Interrupter head Provided 
Mechanism of interrupter.

Method of tripping.
	Y/N
	…………..
…………..
…………..
	…………..
…………..
…………..

	13
	Number of series breaks per phase
	
	…………..
	…………..

	14.
	Minimum total air gap between poles of the same phase
	
mm
	…………..
	…………..

	15.
	Minimum open contact withstand voltage at 50 Hz
	
kV
	…………..
	…………..

	16.
	Minimum open contact impulse withstand voltage 
	kV peak
	…………..
	…………..

	17
	Minimum clearance in air:
	
	
	

	
	a) between poles of a different phase
	mm
	…………..
	…………..

	
	b) Live parts to earth
	mm
	…………..
	…………..

	17.
	Mechanical strength of Insulator stacks:
	
	
	

	
	a) Bending.
	Nm
	…………..
	…………..

	
	b) Torsion.
	Nm
	…………..
	…………..

	18.
	Torque required to operate
	Nm
	…………..
	…………..

	19.
	Dimensions:
	
	
	

	
	a) Height
	mm
	…………..
	…………..

	
	b) Overall Length
	mm
	…………..
	…………..

	
	c ) Minimum phase clearance
	mm
	…………..
	…………..

	20.
	Weight:
	
	
	

	
	a) Isolator, One phase
	Kg
	…………..
	…………..

	
	b) Isolator, Three phase total
	Kg
	…………..
	…………..

	21
	Total creepage distance over of complete isolator insulator
	
mm
	…………..
	…………..

	22
	Protected leakage distance over of complete isolator insulator (90 deg. shadow)
	
mm
	…………..
	…………..

	23
	Has type tests been performed successfully?
	(Y/N)
	…………..
	…………..

	24
	Has type tests been performed in european STL members (KEMA, CESI … etc.)?
	(Y/N)
	…………..
	…………..

	25
	Has a – 1000 h salt fog test - according to the latest edition of IEC 62217.been performed successfully? 
	
(Y/N)
	---------------
	---------------

	26
	No. of years the specified silicone rubber  composite tension insulator has been in production?
	
Year
	---------------
	---------------

	27
	Experience in silicone rubber  composite insulator manufacturing
	
Year
	---------------
	---------------


SCHEDULE e
DRAWINGS and MAINTENANCE INSTRUCTIONS

All drawings shall be to scale and fully detailed.  All important dimensions shall be given and the material of which each part is to be constructed shall be indicated.

Drawings for approval shall be submitted in duplicate as paper prints and, after having approved, the Supplier shall supply any further copies required by the Engineer, one copy at least being a reproduction tracing cloth or approved plastic film. 

MAINTENANCE INSTRUCTIONS
Before the completion date  for the first batch of isolators the Contractor shall submit full Maintenance Instructions, and shall supply such further copies as may be required by the Engineer.

The following is a list of drawings which shall be submitted by the Tenderer with this offer:-

(a)
Outline and arrangement drawings of isolators, structures, clamps/connectors and all other items of plant and equipment covered by this Specification.

(b)
Dimensional drawing of switchgear primary terminals and proposed clamp/connection plate arrangement.

(c)
Detail drawings of HV and LV insulators including electrical characteristics and creepage distances.

(d)
Drawings of all lables.

SCHEDULE e
DRAWINGS and MAINTENANCE INSTRUCTIONS
Outline illustrative Diagram Showing pole mounted type load break isolator for both horizontal and vertical Arrangement with important dimensions for installation purposes:

[image: image2.png]nnnnn




          [image: image3.png]


                    

[image: image1.jpg]



sCHEDULE f
STANDARDS

The Tenderer shall list the standard specifications to which the main items of tendered equipment are designed and manufactured.  

	Equipment
	National Standard
	English Title

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	


SCHEDULE G1 
list of equipment

Item 1:  36 kV POLE MOUNTED TYPE LOAD BREAK ISOLATORS
36 kV, 400 A, 25 kA for 3 seconds, 3-phase outdoor pole mounted load break isolator switches suitable for breaking load current and as follows:.
a)
1-36 kV triple pole open type outdoor load break isolator complete with manually operated mechanism, drive linkage, 400 Amperes at a power factor of 0.75, with clamp connectors  and shall be provided with triple pole set of interrupter heads suitable for breaking load current, and silicone rubber post insulators per each phase, The isolator shall be fully in accordance with IEC 62271-102 and shall be suitable for operation on a system having a fault capacity of 25 kA for 3 seconds.

b)
6- Bimetallic clamp connectors suitable for terminating stranded copper conductor up to 95 sq. mm. and ACSR up to 150 sq.mm. cross section.

The isolators shall be complete with the necessary steelwork for either vertical or horizontal mounting on a lattice steel H-pole with an operating rod height of 11 meters above ground level.

schedule g2 
quantities with prices
*This schedule shall be filled by the tenderers.

	Item
	
Description
	
QTY
	Manufacturer

Name & Origin
	Type (Model Number)
	unit firm CFR price to Aqaba Port

(Currency)
	Total firm CFR price to Aqaba Port

(Currency)
	Delivery

(weeks)

	1.
	36 kV, 400 A, 25 kA for 3 seconds, 3-phase pole mounted load break isolator switches.
	250
 Set
	
	
	
	
	

	1.1
	Ditto as in item1 but with 630A current rating.
	250
 Set
	
	
	
	
	


schedule j
recommended spares for Drop Out Fused Isolator
Prices, quantities and descriptions of spare parts and maintenance equipment  recommended by the Tenderer for the requirements of the Overhead Line Equipment stated in Schedules 'G' and 'H', acceptance of which shall be at the option of the Employer.

	
Description of Spares Recommended
	Quantity
Required
	Unit Firm Price
	Total Firm CFR Price

	- Shaft for 36 kV Isolators**
	5
	…………….
	…………

	- Operating driver for 36 kV Isolators **
	5
	…………….
	…………

	- Operating handle for 36 kV Isolators **
	5
	…………….
	…………

	- Interrupter head for 36 kV Isolators **
	5
	…………….
	…………

	- 3 meters pipe threaded from both sides.
	5
	…………….
	…………

	- 1.5 meters pipe threaded from both sides.
	5
	…………….
	…………

	
	
	…………….
	…………

	
	
	…………….
	…………

	
	
	…………….
	…………

	
	
	…………….
	…………

	
	
	…………….
	…………….

	
	
	…………….
	…………….

	
	
	…………….
	…………….

	
	
	…………….
	…………….

	
	
	…………….
	…………

	GRAND TOTAL FIRM CFR CONTRACT PRICE OF SPARES
	
	
…………


* NOTE: To be included in Schedule 'G'.  

** To be included in the list of spares recommended.

schedule K
deviations from specification

(a) It will be assumed that the plan offered will conform to the Specification in all respects unless deviations are mentioned in this Schedule.  

(b) The Purchaser may waive any minor informality, non-conformity or irregularity in an offer that does not constitute a material deviation provided such waiver does not prejudice or affect the ranking of any Tenderer.  Major deviations in the opinion of the Engineer will render the bid non‑responsive.  
(c) If, upon completing manufacturing and during inspection and delivery process, it is found that certain items that are required and clearly stated in the technical specifications but not included in the final product are not declared in the schedule of deviations (K), then the technical specifications shall prevail and the manufacturer shall be responsible for adding these items to fulfill all requirements called for in the specification at his own cost unless otherwise agreed with the Engineer.

schedule l
list of special tools and equipment required for maintenance purposes
List of Special Tools and Equipment to be provided by the Contractor for maintenance purposes and included in the bid price.  

schedule n
transport facilities

General
It shall be the responsibility of the Contractor to arrange for the shipment of all equipment from the country of origin to the Port of Entry in the Hashemite Kingdom of Jordan.  

Seafreight

When equipment is shipped by sea it must be consigned to the Port of Aqaba.  

Transfer of equipment from ship to shore is normally done by mobile crane or ships derricks, otherwise by lighters which have a maximum capacity of 500 tonnes.  Unloading from the lighter to the quay is limited to a maximum lift of 10 tonnes by means of a mobile crane.  

Roll-on and roll-off facilities are also available for containerized goods.  Containerized goods may be consigned to Amman for customs clearance.  

For special heavy loads a ‘Z’ craft is available in the harbour onto whica heavy trailer can be manoeuvred from a special base constructed for this purpose.  

Trailers with a loading capacity of up to 40 tonnes are available in Jordan and therefore the limit of weight which can be handled depends entirely on the capacity of the ships derricks.  

Transport from the Port normally is on 340 km of rough road although there is a rail head at Ma’an (100 km north of Aqaba).  The rail gauge is 1050 mm and the rail company possesses eighteen “flats” each with a maximum capacity of 15 tonnes.  

Airfreight

When airfreight of equipment is authorized it must be consigned to Queen Alia International Airport, Amman.  

Any goods to be shipped by air may be made by eligible airlines in accordance with Clause 1.4 of Instructions to Bidders.  The Jordanian International Airport is Amman’s Queen Alia International Airport (QAIA).  The Royal Jordanian airlines have direct services to this airport.  

schedule t
test certificate and reference list
It shall be the responsibility of the Contractor to provide all test certificates and reference list for the required items with the submitted offer.
* 	Unless otherwise specified.


*	Materials and apparatus shall be tested at the Maker's Works in accordance with the appropriate National/International Specifications or equivalent specifications which may be applicable.





PAGE  

